|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Sample | Sample | Sample ID | Lead | Copper |
| Location | Date | Number | (ppb) | (ppb) |
| Wastewater Treatment Plant's Lab Sink | 9/11/2019 | 701 | 24 | 480 |
| Bell Atlantic/Bell of PA Building Lower Level Men's Room Sink | 9/11/2019 | 702 | ND | 180 |
| Hayfield Building Basement Men's Room Sink | 9/11/2019 | 801 | 9 | 90 |
| Student Commons Building's Second Floor Uni-sex Bathroom Sink | 9/11/2019 | 802 | 20 | 110 |
| Murphy Student Services Center Men's Room Sink | 9/11/2019 | 803 | ND | 320 |
| Science Building Upper Level Room S-108A Kitchen Sink | 9/11/2019 | 804 | ND | 280 |
| Modular Unit Men's Room Sink | 9/11/2019 | 807 | 7 | 310 |
| Multi-Purpose (Gym) Building Men's Shower Room Sink | 9/11/2019 | 811 | ND | 300 |
| Hemlock Apartment Housing Office Bathroom Sink | 9/11/2019 | 901 | 772 | 240 |
| Oak Apartment Housing Apartment #3 Kitchen Sink (Model Apt) | 9/11/2019 | 902 | 344 | 110 |
| Hayfield Building First Floor Women's Bathroom Sink | 9/24/2019 | 821 | ND | 120 |
| Hayfield Building First Floor Kitchen Sink | 9/24/2019 | 822 | 10 | 200 |
| Student Commons Building Kitchen Prep Area Small Sink | 9/24/2019 | 825 | ND | 600 |
| Student Commons Building Food Line Small Sink | 9/24/2019 | 826 | ND | 460 |
| Murphy Student Services Center Women's Room Sink | 9/24/2019 | 830 | ND | 390 |
| Murphy Student Services Center Men's Room Sink | 9/24/2019 | 831 | ND | 400 |
| Science Building Lab 117B Prep Room Sink | 9/24/2019 | 835 | ND | 670 |
| Science Building Lab 117 Work Station Sink | 9/24/2019 | 836 | ND | 230 |
| Science Building Lab 117 Work Station Sink | 9/24/2019 | 837 | ND | 90 |
| Modular Unit Women's Room Sink | 9/24/2019 | 840 | ND | ND |
| Hayfield Building Boiler Room Basement Sink | 9/24/2019 | 841 | 9 | 90 |
| Hayfield Building Women's Bathroom Basement Sink | 9/24/2019 | 842 | 25 | 180 |
| Multi-Purpose (Gym) Building Small Women's Room Sink | 9/24/2019 | 845 | ND | 350 |
| Multi-Purpose (Gym) Building Small Men's Room Sink | 9/24/2019 | 846 | ND | 260 |
| Multi-Purpose (Gym) Building Men's Locker Room Sink | 9/24/2019 | 847 | ND | 270 |
| Multi-Purpose (Gym) Building Men's Locker Room Sink | 9/24/2019 | 848 | ND | 330 |
| Bell Atlantic/Bell of PA Building Upper Level Kitchen Sink | 9/24/2019 | 850 | ND | 90 |
| Bell Atlantic/Bell of PA Building Lower Level Kitchen Sink | 9/24/2019 | 851 | ND | 310 |
| Hemlock Apt #1 Kitchen Sink | 9/24/2019 | 903 | ND | 100 |
| Hemlock Apt # 2 Kitchen Sink | 9/24/2019 | 904 | ND | ND |
| Oak Apt #2 Kitchen Sink | 9/24/2019 | 905 | ND | ND |
| Oak Apt #4 Kitchen Sink | 9/24/2019 | 906 | ND | ND |
| Hayfield Building Second Floor Women's Room ADA Stall Sink | 9/27/2019 | 823 | ND | 190 |
| Hayfield Building Second Floor Women's Room Sink | 9/27/2019 | 824 | ND | 180 |
| Nesbitt Academic Commons Building Upstairs Kitchen Sink | 9/27/2019 | 860 | ND | 460 |
| Nesbitt Academic Commons Building Downstairs Kitchen Sink | 9/27/2019 | 861 | ND | 380 |
| Career Services Kitchen Sink | 9/27/2019 | 862 | ND | 550 |
| Student Commons Building Large Kitchen Sink | 9/30/2019 | 827 | ND | 500 |
| Bell Atlantic/Bell of PA Building Upper Level Men's Room Sink | 9/30/2019 | 852 | ND | 100 |
| Bell Atlantic/Bell of PA Building Lower level Men's Room Sink | 9/30/2019 | 853 | ND | 120 |

Values in red font exceed action levels.

Values listed as ND were Not Detected by the laboratory.

The 90th percentile value for our water system is **greater than the lead action level of 15 parts per billion (ppb).** The 90th percentile value for our water system is **less than the copper action level of 1,300 ppb.**